Date of Online View : 06-08-2011

Analysis Report Of MAYAPURI CETP (12 MLD)

Report Number : DPCC/W/CETP/11-12/031. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 08-06-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.6; 5.5-9.0; 7.5; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 360; ...; 112; 250. 4; BOD (3 days at 27o C); 115; ...; 30; 30. 5; Ni; 0.62; 3; 0.20; 3. 6; Cu; 0.52; 3; 0.15; 3. 7; Zn; 1.62; 15; 1.0; 5. 8; Cr (Total); 1.40; 2; 0.68; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 530; ...; 430; 1000. 11; SO4; 39.1; ...; 10.1; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 24.0; 20; 2.8; 10. 14; TDS; 1700; ...; 1600; 2100. 15; Ammonical Nitrogen as N; 18.1; 50; 10.1; 50. 16; Fluoride; 3.2; 15; 2.6; 2. 17; Sulphide; 10.3; ...; 2.5; 2.8.

All values are in mg/l except pH

... No Standards

Flow : 3.0 MLD

SCIENTIST (D); SR SCIENTIFIC ASSISTANT.

| Date of Online View : 06-08-2011Analysis Report Of MAYAPURI CETP (12 MLD) All values are in mg/l except pH ... No Standards ND- Not Detectable Flow : 3.0 MLD Report Number : DPCC/W/CETP/11-12/020 |  |
| --- | --- |
| 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 27-05-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results. |

| S. No | Parameter | Inlet |  | Final Outlet |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Water Quality | EPA Standards | Water Quality | EPA Standards |
| 1 | pH | 7.3 | 5.5-9.0 | 7.9 | 5.5-9.0 |
| 2 | TSS | - | 250 | - | 100 |
| 3 | COD | 316 | ... | 80 | 250 |
| 4 | BOD (3 days at 27o C) | 119 | ... | 26 | 30 |
| 5 | Ni | 0.47 | 3 | 0.09 | 3 |
| 6 | Cu | 0.72 | 3 | 0.11 | 3 |
| 7 | Zn | 1.38 | 15 | 0.88 | 5 |
| 8 | Cr (Total) | 1.24 | 2 | 0.48 | 2 |
| 9 | Pb | ND | 1 | ND | 0.1 |
| 10 | Cl | 700 | ... | 650 | 1000 |
| 11 | SO4 | 45.6 | ... | 36.1 | 1000 |
| 12 | Cd | ND | 1 | ND | 1 |
| 13 | Oil & Grease | 10.2 | 20 | 1.8 | 10 |
| 14 | TDS | 2200 | ... | 1400 | 2100 |
| 15 | Ammonical Nitrogen as N | 11.9 | 50 | 0.38 | 50 |
| 16 | Fluoride | 5.9 | 15 | 4.4 | 2 |
| 17 | Sulphide | 9.2 | ... | 2.8 | 2.8 |

| Date of Online View : 06-08-2011. Analysis Report Of MAYAPURI CETP (12 MLD). Report Number : DPCC/W/CETP/11-12/008. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 21-04-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.1; 5.5-9.0; 7.8; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 368; ...; 112; 250. 4; BOD (3 days at 27o C); 110; ...; 27; 30. 5; Ni; 0.54; 3; 0.16; 3. 6; Cu; 0.36; 3; 0.12; 3. 7; Zn; 1.22; 15; 0.46; 5. 8; Cr (Total); 0.20; 2; ND; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 680; ...; 620; 1000. 11; SO4; 52; ...; 42; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 22.4; 20; 2.4; 10. 14; TDS; 2300; ...; 1800; 2100. 15; Ammonical Nitrogen as N; 16.8; 50; 0.7; 50. 16; Fluoride; 2.9; 15; 2.4; 2. 17; Sulphide; 4.0; ...; ND; 2.8.. All values are in mg/l except pH. ... No Standards. ND- Not Detectable. Flow : 2.5 MLD. SR. SCIENTIST; LAB ASSTT./ SSA.. |  |
| --- | --- |

Date of Online View : 06-08-2011

Analysis Report Of MAYAPURI CETP (12 MLD) Report Number : DPCC/W/CETP/10-11/127. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 09-03-2011. 4; Samples collected by; DPCC LAB.. 5; Parameters analyzed and results..

S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.0; 5.5-9.0; 7.4; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 512; ...; 136; 250. 4; BOD (3 days at 27o C); 135; ...; 28; 30. 5; Ni; 1.84; 3; 0.48; 3. 6; Cu; 0.95; 3; 0.11; 3. 7; Zn; 1.85; 15; 0.83; 5. 8; Cr (Total); 1.21; 2; 0.28; 2. 9; Pb; 0.01; 1; ND; 0.1. 10; Cl; 900; ...; 630; 1000. 11; SO4; 75.3; ...; 68.5; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 9.6; 20; 1.2; 10. 14; TDS; 2900; ...; 2000; 2100. 15; Ammonical Nitrogen as N; 15.7; 50; 6.6; 50. 16; Fluoride; 3.0; 15; 2.1; 2. 17; Sulphide; 7.6; ...; 0.48; 2.8.

All values are in mg/l except pH

... No Standards

ND- Not Detectable

Flow : 2.7 MLD

SR. SCIENTIST; LAB ASSTT./ SSA. Date of Online View : 06-08-2011. Analysis Report Of MAYAPURI CETP (12 MLD). Report Number : DPCC/W/CETP/10-11/120. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 23-02-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 6.4; 5.5-9.0; 7.7; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 580; ...; 120; 250. 4; BOD (3 days at 27o C); 160; ...; 28; 30. 5; Ni; 0.3; 3; ND; 3. 6; Cu; 0.44; 3; 0.10; 3. 7; Zn; 0.64; 15; 0.19; 5. 8; Cr (Total); 0.37; 2; ND; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 220; ...; 160; 1000. 11; SO4; 78; ...; 56; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 10.0; 20; 2.8; 10. 14; TDS; 1800; ...; 1320; 2100. 15; Ammonical Nitrogen as N; 13.0; 50; 7.0; 50. 16; Fluoride; 2.3; 15; 2.1; 2. 17; Sulphide; 4.4; ...; 2.8; 2.8.. All values are in mg/l except pH. ... No Standards. ND- Not Detectable. Flow : 3.0 MLD..

SR. SCIENTIST                                                                                                                                LAB ASSTT. / SSA

Date of Online View : 06-08-2011

Analysis Report Of MAYAPURI CETP (12 MLD)

Report Number : DPCC/W/CETP/10-11/105. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 06-01-2011. 4; Samples collected by; DPCC LAB.. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.5; 5.5-9.0; 7.9; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 520; ...; 136; 250. 4; BOD (3 days at 27o C); 130; ...; 24; 30. 5; Ni; 1.21; 3; 0.40; 3. 6; Cu; 0.52; 3; 0.08; 3. 7; Zn; 1.40; 15; 0.82; 5. 8; Cr (Total); 0.97; 2; 0.14; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 930; ...; 670; 1000. 11; SO4; 51; ...; 49; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 10.0; 20; 4.7; 10. 14; TDS; 3200; ...; 2330; 2100. 15; Ammonical Nitrogen as N; 4.9; 50; 4.9; 50. 16; Fluoride; 0.36; 15; 0.17; 2. 17; Sulphide; 1.9; ...; 4.9; 2.8.

All values are in mg/l except pH

... No Standards

ND- Not Detectable

Flow : 2.5 MLD

SR. SCIENTIST; LAB ASSTT./ SSA.

Date of Online View : 06-08-2011

Analysis Report Of MAYAPURI CETP (12 MLD)

Report Number : DPCC/W/CETP/11-12/031. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 08-06-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.6; 5.5-9.0; 7.5; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 360; ...; 112; 250. 4; BOD (3 days at 27o C); 115; ...; 30; 30. 5; Ni; 0.62; 3; 0.20; 3. 6; Cu; 0.52; 3; 0.15; 3. 7; Zn; 1.62; 15; 1.0; 5. 8; Cr (Total); 1.40; 2; 0.68; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 530; ...; 430; 1000. 11; SO4; 39.1; ...; 10.1; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 24.0; 20; 2.8; 10. 14; TDS; 1700; ...; 1600; 2100. 15; Ammonical Nitrogen as N; 18.1; 50; 10.1; 50. 16; Fluoride; 3.2; 15; 2.6; 2. 17; Sulphide; 10.3; ...; 2.5; 2.8.

All values are in mg/l except pH

... No Standards

Flow : 3.0 MLD

SCIENTIST (D); SR SCIENTIFIC ASSISTANT.

| Date of Online View : 06-08-2011Analysis Report Of MAYAPURI CETP (12 MLD) All values are in mg/l except pH ... No Standards ND- Not Detectable Flow : 3.0 MLD Report Number : DPCC/W/CETP/11-12/020 |  |
| --- | --- |
| 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 27-05-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results. |

| S. No | Parameter | Inlet |  | Final Outlet |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Water Quality | EPA Standards | Water Quality | EPA Standards |
| 1 | pH | 7.3 | 5.5-9.0 | 7.9 | 5.5-9.0 |
| 2 | TSS | - | 250 | - | 100 |
| 3 | COD | 316 | ... | 80 | 250 |
| 4 | BOD (3 days at 27o C) | 119 | ... | 26 | 30 |
| 5 | Ni | 0.47 | 3 | 0.09 | 3 |
| 6 | Cu | 0.72 | 3 | 0.11 | 3 |
| 7 | Zn | 1.38 | 15 | 0.88 | 5 |
| 8 | Cr (Total) | 1.24 | 2 | 0.48 | 2 |
| 9 | Pb | ND | 1 | ND | 0.1 |
| 10 | Cl | 700 | ... | 650 | 1000 |
| 11 | SO4 | 45.6 | ... | 36.1 | 1000 |
| 12 | Cd | ND | 1 | ND | 1 |
| 13 | Oil & Grease | 10.2 | 20 | 1.8 | 10 |
| 14 | TDS | 2200 | ... | 1400 | 2100 |
| 15 | Ammonical Nitrogen as N | 11.9 | 50 | 0.38 | 50 |
| 16 | Fluoride | 5.9 | 15 | 4.4 | 2 |
| 17 | Sulphide | 9.2 | ... | 2.8 | 2.8 |

| Date of Online View : 06-08-2011. Analysis Report Of MAYAPURI CETP (12 MLD). Report Number : DPCC/W/CETP/11-12/008. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 21-04-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.1; 5.5-9.0; 7.8; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 368; ...; 112; 250. 4; BOD (3 days at 27o C); 110; ...; 27; 30. 5; Ni; 0.54; 3; 0.16; 3. 6; Cu; 0.36; 3; 0.12; 3. 7; Zn; 1.22; 15; 0.46; 5. 8; Cr (Total); 0.20; 2; ND; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 680; ...; 620; 1000. 11; SO4; 52; ...; 42; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 22.4; 20; 2.4; 10. 14; TDS; 2300; ...; 1800; 2100. 15; Ammonical Nitrogen as N; 16.8; 50; 0.7; 50. 16; Fluoride; 2.9; 15; 2.4; 2. 17; Sulphide; 4.0; ...; ND; 2.8.. All values are in mg/l except pH. ... No Standards. ND- Not Detectable. Flow : 2.5 MLD. SR. SCIENTIST; LAB ASSTT./ SSA.. |  |
| --- | --- |

Date of Online View : 06-08-2011

Analysis Report Of MAYAPURI CETP (12 MLD) Report Number : DPCC/W/CETP/10-11/127. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 09-03-2011. 4; Samples collected by; DPCC LAB.. 5; Parameters analyzed and results..

S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.0; 5.5-9.0; 7.4; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 512; ...; 136; 250. 4; BOD (3 days at 27o C); 135; ...; 28; 30. 5; Ni; 1.84; 3; 0.48; 3. 6; Cu; 0.95; 3; 0.11; 3. 7; Zn; 1.85; 15; 0.83; 5. 8; Cr (Total); 1.21; 2; 0.28; 2. 9; Pb; 0.01; 1; ND; 0.1. 10; Cl; 900; ...; 630; 1000. 11; SO4; 75.3; ...; 68.5; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 9.6; 20; 1.2; 10. 14; TDS; 2900; ...; 2000; 2100. 15; Ammonical Nitrogen as N; 15.7; 50; 6.6; 50. 16; Fluoride; 3.0; 15; 2.1; 2. 17; Sulphide; 7.6; ...; 0.48; 2.8.

All values are in mg/l except pH

... No Standards

ND- Not Detectable

Flow : 2.7 MLD

SR. SCIENTIST; LAB ASSTT./ SSA. Date of Online View : 06-08-2011. Analysis Report Of MAYAPURI CETP (12 MLD). Report Number : DPCC/W/CETP/10-11/120. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 23-02-2011. 4; Samples collected by; DPCC Lab. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 6.4; 5.5-9.0; 7.7; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 580; ...; 120; 250. 4; BOD (3 days at 27o C); 160; ...; 28; 30. 5; Ni; 0.3; 3; ND; 3. 6; Cu; 0.44; 3; 0.10; 3. 7; Zn; 0.64; 15; 0.19; 5. 8; Cr (Total); 0.37; 2; ND; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 220; ...; 160; 1000. 11; SO4; 78; ...; 56; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 10.0; 20; 2.8; 10. 14; TDS; 1800; ...; 1320; 2100. 15; Ammonical Nitrogen as N; 13.0; 50; 7.0; 50. 16; Fluoride; 2.3; 15; 2.1; 2. 17; Sulphide; 4.4; ...; 2.8; 2.8.. All values are in mg/l except pH. ... No Standards. ND- Not Detectable. Flow : 3.0 MLD..

SR. SCIENTIST                                                                                                                                LAB ASSTT. / SSA

Date of Online View : 06-08-2011

Analysis Report Of MAYAPURI CETP (12 MLD)

Report Number : DPCC/W/CETP/10-11/105. 1; Name & Address of Ind./ Unit; MAYAPURI CETP (12 MLD). 2; Sampling location; Inlet and Outlet of CETP. 3; Date of sampling; 06-01-2011. 4; Samples collected by; DPCC LAB.. 5; Parameters analyzed and results.. S. No; Parameter; Inlet; Final Outlet. Water Quality; EPA Standards; Water Quality; EPA Standards. 1; pH; 7.5; 5.5-9.0; 7.9; 5.5-9.0. 2; TSS; -; 250; -; 100. 3; COD; 520; ...; 136; 250. 4; BOD (3 days at 27o C); 130; ...; 24; 30. 5; Ni; 1.21; 3; 0.40; 3. 6; Cu; 0.52; 3; 0.08; 3. 7; Zn; 1.40; 15; 0.82; 5. 8; Cr (Total); 0.97; 2; 0.14; 2. 9; Pb; ND; 1; ND; 0.1. 10; Cl; 930; ...; 670; 1000. 11; SO4; 51; ...; 49; 1000. 12; Cd; ND; 1; ND; 1. 13; Oil & Grease; 10.0; 20; 4.7; 10. 14; TDS; 3200; ...; 2330; 2100. 15; Ammonical Nitrogen as N; 4.9; 50; 4.9; 50. 16; Fluoride; 0.36; 15; 0.17; 2. 17; Sulphide; 1.9; ...; 4.9; 2.8.

All values are in mg/l except pH

... No Standards

ND- Not Detectable

Flow : 2.5 MLD

SR. SCIENTIST; LAB ASSTT./ SSA.

| SCIENTIST (D) | SR SCIENTIFIC ASSISTANT |
| --- | --- |

| SCIENTIST (D) | SR SCIENTIFIC ASSISTANT |
| --- | --- |